## Slide 1
L1 - Copperplate | L2 - 7 aggregated Nodes | L3/L3+/L3NL - 15 Nodes
HP
CHP
Boiler
aggregated heat demand
HP
CHP
Boiler
Heat losses, Spatial structure
Transport delay, Pressure drop,
Temperature gradient
No losses, no spatial structure
CHP
Boiler
HP
Full topolpgy resolution,
Different thermo-hydraulic physics
+ 10,5%
+ 13,0%
+ 13,1%
+ 13,5%
CO2
74 t CO2
underestimated
Topology Resolution Dominates Dispatch Accuracy in District Heating Networks with industrial loads:
A Five-Level MILP Comparison
Key findings
This study isolated 5 modeling dimensions for DH dispatch (topology and thermo-hydraulics). Casestudy for a heating grid (12MW, 8760h) and 36 synthetic grids.
topology dominates thermo-hydraulics
Copperplate underestimate cost by 13%
L1 | L2 | L3 | L3+ | L3NL
cumulative cost deviation from L1

## Slide 2
CP - Copperplate | ZN - 7 aggregated Zones | L1/L2/L3 - 15 Nodes | L4/L5/L6 - 174 Stations
Estimation Bias versus Decision Regret in industrial District-Heating Dispatch Optimisation
Key Findings: Loss visibility, not spatial layout, is decisive: the copperplate-to-detailed cost gap is 95.8 % a loss effect and only 4.7 % a topology effect. On operating cost a copperplatescores -15.1 % against the detailed model, but +46.1 % once its schedule is run: a biased estimatorand an unreliable controller at once.
Loss visibility
Spatial topology
Loss and topology interaction
Tem.p propagation
Pres. drop & pumping
Station res.
Dynamic pressure
Trans. delay

## Slide 3
copperplate | Zone-resolved model | Node-resolved model | Station-resolved model
Increasing spatial detail and hydraulic fidelity
Loss Visibility versus Spatial Detail in industrial District-Heating Dispatch Optimisation
Key Findings: Model heat losses explicitly. Under central generation in radial networks, additional spatial and station-level detail provides limited dispatch value.